To

Nahar Spining Mills Limited
375, Industrial Area – A
Ludhiana
Punjab

Sub: Vibration of Nahar Tower

Sub: Solution to Vibration of Building

Request 12/08/2015

Sub: Vibration of Nahar Tower

Sir,

In response to you request dated 12/08/2015 for “Solution to Vibration of Building”, find attached our report for your kind consideration.

With regards,

Report

Building	Nahar Tower
Client	Nahar Spining Mills Limited
Address	375, Industrial Area – A, Ludhiana, Punjab
Issue	Vibrations
Observations	The vibration study of Nahar Tower was conducted on Sept 2, 2015. Vibration in building (due to operation of hammer of nearby Industries) recorded on various parts of building was found to have average of peak acceleration of 0.72 m/s2 with a SD of 0.051 m/s2 , with maximum peak value of 0.82 m/s2.
Inference	The above mentioned average peak acceleration was 7.33% of g (acceleration due to gravity) and maximum peak acceleration was observed as 8.36% of g. The parameter is not of a magnitude to cause any distress / fatigue in the structural member*a. / The effect of vibration is equivalent to that of “Traffic (road, rail)”, “Machinery inside building” *b.
Remedy	It is recommended to provide a floor rubber mat in the office building to reduce the vibration / acceleration being felt by the occupants.
* Source	[a] Construction Technology Update No. 22, NRC-CNRC, Published by Institute for Research in Construction. / [b] ISO 4866:1990 Evaluation and measurement for vibration in buildings: Part 1.